## Initial List of Constraints
|  | Highlight potential candidates for geotargeting |  |  |  | If not load growth related, then N
If year of need is less than 2 years or greater than 10, then N
This page reserved for the initial list of constraints as identified in LRTP and utilities.
Only fill these columns if constraint is load growth related
Constraint | Load Growth related (Y/N) | Project Update | MW need** | Year of need | Zonal identified MW available (potential study) | Further screening (Y/N) (If not load growth related, N. If yr of need <2 or >10, N.)

## 6290 Screening
Jackson Corners Substation Rebuild
Use this form for Substation Projects
Number | Questions | Example | yes | no |  | Hinesburg #19 Substation | Hinesburg Transformer Upgrade
1 | Cost of the Upgrade greater than $2,000,000 (If so, check “Yes” and continue to Line 4; otherwise check “No” and. continue to Line 2 ) | Any T&D project whose capital cost is expected to exceed $2 million (in year 2002 dollars, adjusted for inflation in future years), including any reasonably foreseeable related projects, sub-projects, and multiple phases, should be reviewed for the applicability of DUP. | x |  |  | no | no
2 | Relieves T & D delivery constraing in Capacity Constrained Area (If so, check “Yes” and continue to Line 3; otherwise check “No” and exclude the expected upgrade from DU analysis.) | DUs may exclude from DUP analysis Non-Constrained Area Projects, as defined in the Docket No. 6290 MOU, of $2 million or less (determined as described in the note to line 1). |  |  |  | no | no
3 | Cost of the Upgrade less than $250,000 (If so, check “Yes” and exclude the expected upgrade from DU analysis; otherwise check “No” and continue to Line 4.) | Projects of less than $250,000 (in year 2002 dollars, adjusted for inflation in future years) may be excluded from DUP analysis. This step is intended to identify constrained situations in which the DU study would be disproportionately costly, compared to the budgeted project cost. |  |  |  | no | no
4 | Upgrade driven by emergency situation requiring immediate replacement of equipment that has failed or is at immenent risk of failure (If so, check “Yes” and exclude the upgrade from DU analysis; otherwise check “No” and continue to line 5. ) | Minor projects that are only parts of a larger project should not be screened using this step. For example, a substation rebuild would include many of the items listed in 5.a–j, but would not be a project that is minor in size and scope. Therefore, larger projects such as substation rebuilds should be analyzed according to the criteria in lines 7 through 12. |  | x |  | no | no
5 | Does the upgrade constitute a minor change for the purpose of system tuning of efficency improvements (If so, check “Yes,” indicate which of the below upgrades are included (check all that apply), and exclude the upgrade from DU analysis. Otherwise check “No” and continue to line 6. ) | These situations do not include upgrading equipment specifically to significantly increase capacity, which should be reviewed at lines 11 and 12. |  | x |  | no | no
5.a | Installation or changes to relays, reclosers, fuses, switches, sectionalizers, breakers, breaker bypass switches, MOABs, capacitors, regulators, arresters, insulators, or meters | These situations do not include upgrading equipment specifically to significantly increase capacity, which should be reviewed at lines 11 and 12. |  |  |  | yes | yes
5.b | Installation or replacement of underground getaways |  |  |  |  | no | no
5.c | Upgrade of substation bus work |  |  |  |  | yes | no
5.d | Upgrade of substation structural work, fencing, or oil containment |  |  |  |  | yes | yes
5.e | Installation or upgrade to SCADA |  |  |  |  | yes | no
5.f | Transformer Swaps |  |  |  |  | yes | yes
5.g | Addition of fans to transformers |  |  |  |  | yes | yes
5.h | Balancing of feeder phases |  |  |  |  | no | no
5.i | Replacement of deteriorated poles, crossarms, structures, poles and conduit; and replacement of wires on such equipment with the least-cost wires. (See note.) |  |  |  |  | yes | no
5.j | Other (please describe):
6 | Is the upgrade a line-reconstruction project pursuant to joint use agreements with telephone or CATV or pole-attachment tariff requirements? (If so, check “Yes” and exclude the upgrade from DU analysis; otherwise check “No” and continue to line 7. ) |  |  | x |  | no | no
7 | Is the upgrade the result of a customer’s request for a specific equipment or service for which distributed resources would not be acceptable? (If so, check “Yes,” describe the situation, and exclude the expected upgrade from DU analysis; otherwise check “No” and continue to line 8. ) | For example, the customer may be willing to pay for a distribution upgrade, but not for distributed resources. In other situations, the customer may be willing to pay for distributed resources, but may be unwilling to have the distributed resources on its premises, and resources elsewhere may not provide the required service. |  | x |  | no | no
8 | Is the upgrade required to remedy reliability, stability, or safety problems? (If so, check “Yes” and continue to line 9; otherwise check “No” and skip to line 11. ) |  | x |  |  | yes | yes
9 | Could the scope and cost of the resulting project be reduced by a reduction in load level or by the installation of distributed generation? (If so, check “Yes” and continue to line 10; otherwise check “No” and skip to line 11.) | If reduction in present load by 25% and the elimination of all load growth would not affect the need for the project, or its cost, the project may be considered to be independent of load. The feasibility of the required load reductions will be reviewed in the resource-scoping stage of the DU analysis. The determination that load reductions would not avoid a particular investment can be established by reference to an approved policy (such as standards adopted to capture lost opportunities or simplify system operations). If so, indicate the document that specifies the policy. | x |  |  | no | yes
10 | Is the likely reduction in costs from the potential reduction in scope less than $250,000? (If so, check “Yes” and exclude the upgrade from DU analysis; otherwise check “No” and continue to line 11.) | The $250,000 is in year 2002 dollars, to be adjusted for inflation in future years. | x |  | a $112,000 differential in cost between replacing the transformer with a 3.75 KVA and replacing it with a 7.5 kVA transformer. This is well below the $250,000 cost threshold even before applying inflation adjustment (roughly $450,000 in 2025 dollars). |  | no
11 | Would load reduction or generation allow for the elimination or deferral of all of the upgrade? (If so, check “Yes” and proceed to define the scope and timing of the local DU analysis; otherwise check “No” and continue to line 12.) | If reduction in present load by 25% and the elimination of all load growth would not affect the need for the project, or its cost, the project may be considered to be independent of load. The feasibility of the required load reductions will be reviewed in the resource-scoping stage of the DU analysis. The determination that load reductions would not avoid a particular investment can be established by reference to an approved policy (such as standards adopted to capture lost opportunities or simplify system operations). If so, indicate the document that specifies the policy. |  |  |  | no | yes
12 | Can the upgrade be implemented with different levels of capacity in the replacement equipment, with costs that could differ by more than $250,000? (If not, check “No” and exclude the expected upgrade from DU analysis; otherwise check “Yes” and proceed to define the scope and timing of the local DU analysis.) | The $250,000 is in year 2002 dollars, to be adjusted for inflation in future years. |  |  |  | no | no

## 7081 Screening
Use this form for Transmission Projects
Number | Questions
1a | Needed for a redundant supply to radial load
1b | Maintenance-relaetd, addressing asset condition, operations, safety
1c | Addressing trasmission performance, addition of high speed protection or a switch to sectionalize a line
1d | Needed to address stability or short circuit problems
1e | Other technical reason why NTAs are impractical
2 | Proposed tranmission project need date
3 | Could elimination or deferral of all or part of the upgrade be accomplished by a 25% or smaller load reduction or off-setting generation of the same magnitude. (If "no", project screens out of NTA analysis)
4 | Is the likely reduction in costs from the potential elimination or defferal of all or part of the upgrade greater than $2.5 million (If "no", project screens out of NTA analysis)

## Fairfax 12 Transformer (hidden)
AREA NAME
Updated 06/19/2018 |  |  | RECOMMENDATION: This project is excluded from NTA analysis per the Docket 6290 screening tool. Upgrade being done for load growth
Blue Background = Info provided by DU
Orange Background = Info provided by EEU
Instructions
Information regarding the constraint
T&D Constraint Name | Fairfax 12 Transformer Upgrade
Primary Justification | Load Growth
Description of Constraint | The substation load at the Fairfax 12 substation exceeds 80% of base rating MVA which is in violation of VEC's design criteria. There are currently 2 x 833 kVA transformers both of which would need to be upgraded. In certain areas of VEC’s system such as the Fairfax the load is primarily driven by sugar makers. The load presents a challenge from a planning perspective as it occurs for 3-4 weeks, 24 hours a day, in the spring. As such the increased flexibility that this project would provide would greatly enhance service and reliability to the area.
Description of Upgrade | This project upgrades the two existing 833 kVA transformers at VEC’s Fairfax 12 substation to three 1667 kVA at transformers. This will allow for future load growth and for a future project to build three phase feeder backup between Fairfax 12 and Fairfax 1. |  |  | Forecasted load and EE Incremental to Statewide
VSPC Load Zone | B | Could be one or more |  | Critical Load Level |  |  |  | Transformer Max 2 x 844 KVA | From Cell B14 | VT
Season of Issue | Spring | Winter, Summer, or Both |  | Year | 50/50 forecast (MW) [N2] | 90/10 forecast (MW) [N1] | "High Scenario" (MW) | Incremental GT EE needed [N3] | Note 1- use CELT forecast 50/50 to 90/10 ratio provided to the right for relevant ratio. Carry 2020 ratio out for 10 years | SUMMER | 90% | 80% | 70% | 60% | 50% | 40% | 30% | 20% | 10% | 5% | 1950-10-01
Most Recent Peak Load | 1.612 MVA (4/8/2015 7:00:00 PM) |  |  | 2012 | [5 empty] | 2011 | 1030 | 1035 | 1040 | 1050 | 1070 | 1075 | 1090 | 1095 | 1110 | 1110 | 1.0374
5-year historical maximum peak Load |  |  |  | 2013 |  |  |  |  | Note 2 - these loads should already be adjusted for EE included in the trend forecast (removed per EVT reports for every year of the weighted average) then statewide expected savings added (per VEIC calculation, PSB ordered budgets) | 2012 | 1050 | 1055 | 1060 | 1070 | 1090 | 1095 | 1115 | 1120 | 1125 | 1135 | 1.0321
Known additional load | None | e.g. from "Ability to Serve" letters |  | 2014 | [5 empty] | 2013 | 1065 | 1070 | 1075 | 1085 | 1105 | 1110 | 1130 | 1135 | 1150 | 1150 | 1.0407
Critical Load Level | Transformer Max 2 x 844 KVA |  |  | 2015 | [5 empty] | 2014 | 1080 | 1085 | 1090 | 1100 | 1120 | 1125 | 1145 | 1150 | 1165 | 1170 | 1.0402
Load Reduction Needed | See Column I to the right |  |  | 2016 | [5 empty] | 2015 | 1095 | 1100 | 1105 | 1115 | 1135 | 1140 | 1160 | 1165 | 1170 | 1180 | 1.0308
Load Reduction Needed from EE |  | recognizing that NTA option might include a number of different NTAs which EE is one. Provide forecast information. Does forecast assume statewide EE programs already? |  | 2017 | [5 empty] | 2016 | 1105 | 1110 | 1115 | 1125 | 1145 | 1150 | 1170 | 1175 | 1190 | 1195 | 1.0393
Relavent VSPC Load Zone Maximum Achievable Savings Potential |  | From EEU achievable potential study |  | 2018 |  |  |  |  | Explanation of "High Scenario" parameters: | 2017 | 1115 | 1120 | 1125 | 1135 | 1155 | 1160 | 1180 | 1185 | 1195 | 1205 | 1.0346
Annual Exposure Duration (hours) |  | Attach documents as appropriate |  | 2019 | [5 empty] | 2018 | 1125 | 1130 | 1140 | 1150 | 1170 | 1175 | 1195 | 1200 | 1215 | 1215 | 1.0385
Constrained Area Peak Time of Day |  | range acceptable |  | 2020 | [5 empty] | 2019 | 1135 | 1140 | 1150 | 1160 | 1180 | 1185 | 1205 | 1210 | 1225 | 1230 | 1.0381
Estimated Year Project Needed absent GT | From Columns E-I to right when Cell B 14 critical load level > column H | If 2 years or less, then may not be viable for GT. If over 10 years, then may not be viable for GT. |  | 2021 | [5 empty] | 2020 | 1145 | 1150 | 1155 | 1170 | 1190 | 1195 | 1215 | 1225 | 1235 | 1240 | 1.0378
Estimated Project Cost $ |  | Use current year $ |  | 2022 | [5 empty] | WINTER
Benefit Classification |  | Use VSPC classification of system level and affected utilities - see 7081 definitions |  | 2023 |  |  |  |  | Note 3 - Incremental GT EE Needed should be defined as the level of incremental EE needed to keep the forecasted load below the critical load level | 2011/2012 | 1030 | 1035 | 1035 | 1035 | 1045 | 1050 | 1055 | 1055 | 1060 | 1070 | 1.0144
Estimated Annual Deferral Value |  | to determine real levelized carrying charge use method as defined in Docket 7081 MOU paragraph 63 |  | 2024 | [5 empty] | 2012/2013 | 1040 | 1045 | 1045 | 1045 | 1055 | 1060 | 1065 | 1065 | 1070 | 1080 | 1.0142
|  |  |  | 2025 | [5 empty] | 2013/2014 | 1050 | 1055 | 1055 | 1055 | 1065 | 1070 | 1075 | 1075 | 1080 | 1095 | 1.0141
Deferral Value |  |  |  | 2026 | [5 empty] | 2014/2015 | 1055 | 1060 | 1060 | 1060 | 1070 | 1075 | 1080 | 1080 | 1085 | 1095 | 1.014
Number of Years EE is able to defer project |  |  |  | 2027 | [5 empty] | 2015/2016 | 1060 | 1065 | 1065 | 1065 | 1075 | 1080 | 1085 | 1085 | 1090 | 1110 | 1.014
Value of deferment |  |  |  | 2028 | [5 empty] | 2016/2017 | 1065 | 1070 | 1070 | 1070 | 1080 | 1085 | 1090 | 1090 | 1100 | 1110 | 1.0185
Value of any additional T&D benefits provided by EE |  | e.g. reducing risk of contingencies, etc. Describe - could be narrative |  | 2029 | [5 empty] | 2017/2018 | 1075 | 1080 | 1080 | 1080 | 1090 | 1095 | 1100 | 1100 | 1105 | 1120 | 1.0138
reducing risk of unanticipated load coming on-line |  |  |  | 2030 | [5 empty] | 2018/2019 | 1080 | 1085 | 1085 | 1085 | 1095 | 1100 | 1105 | 1105 | 1110 | 1120 | 1.0137
reducing existing exposure on bulk transmission system |  |  |  | 2031 | [5 empty] | 2019/2020 | 1085 | 1090 | 1090 | 1090 | 1100 | 1105 | 1110 | 1110 | 1115 | 1125 | 1.0136
reducing existing exposure on subtransmission system | [9 empty] | 2020/2021 | 1090 | 1095 | 1095 | 1095 | 1105 | 1110 | 1115 | 1115 | 1120 | 1130 | 1.0136
reducing existing exposure on distribution system
Back to Main Page

## Cambridge 03 (hidden)
AREA NAME
Updated 05/25/2016 |  |  | RECOMMENDATION: This project is excluded from NTA analysis per the Docket 6290 screening tool. Upgrade being done for reliability and asset managmenet
Blue Background = Info provided by DU
Orange Background = Info provided by EEU
Instructions
Information regarding the constraint
T&D Constraint Name | Cambridge 03
Primary Justification | Reliability and Asset Management (Age and Condition)
Description of Constraint | Since 2008 there have been 19 power supplier (GMP) outages which have resulted in 39,798 customer hours out to the customers of VEC Johnson, Cambridge, Madonna, and Pleasant Valley as well as customers of GMP Jeffersonville. These outages also have a significant impact on VEC's fourth largest customer account, Smugglers Notch. There is no existing automated protection from GMP Johnson to VELCO East Fairfax.
Description of Upgrade | VEC will rebuild the substation with GMP on the existing site. GMP will split the cost, design, permitting, and construction of the project with VEC (referenced in JOA). A second tranmission tap on the GMP owned tranmission line will be built to the substation. Two new high side vaccuum breakers will be added and the existing B7 will be replaced with a new vaccum breaker. The existing substation switches will be replaced, but the existing recloser and regulators will be used. A new single phase 351RS recloser will be installed to serve the members on the current 1Y . The transformer will be replaced with a 3-phase 5/6.25 MVA with concrete oil containment. The oil containment may need to be pumped out periodically due to a lack of sufficient grade for a daylight drain. VEC will build and construct the susbstation with assistance from TBD contractors or GMP where needed. |  |  | Forecasted load and EE Incremental to Statewide
VSPC Load Zone | C | Could be one or more |  | Critical Load Level |  |  |  | Transformer Max 2.5 MVA | From Cell B14 | VT
Season of Issue | Both | Winter, Summer, or Both |  | Year | 50/50 forecast (MW) [N2] | 90/10 forecast (MW) [N1] | "High Scenario" (MW) | Incremental GT EE needed [N3] | Note 1- use CELT forecast 50/50 to 90/10 ratio provided to the right for relevant ratio. Carry 2020 ratio out for 10 years | SUMMER | 90% | 80% | 70% | 60% | 50% | 40% | 30% | 20% | 10% | 5% | 1950-10-01
Most Recent Peak Load | 1.612 MVA (4/8/2015 7:00:00 PM) |  |  | 2012 | [5 empty] | 2011 | 1030 | 1035 | 1040 | 1050 | 1070 | 1075 | 1090 | 1095 | 1110 | 1110 | 1.0374
5-year historical maximum peak Load | 1.612 MVA (4/8/2015 7:00:00 PM) |  |  | 2013 |  |  |  |  | Note 2 - these loads should already be adjusted for EE included in the trend forecast (removed per EVT reports for every year of the weighted average) then statewide expected savings added (per VEIC calculation, PSB ordered budgets) | 2012 | 1050 | 1055 | 1060 | 1070 | 1090 | 1095 | 1115 | 1120 | 1125 | 1135 | 1.0321
Known additional load | None | e.g. from "Ability to Serve" letters |  | 2014 | [5 empty] | 2013 | 1065 | 1070 | 1075 | 1085 | 1105 | 1110 | 1130 | 1135 | 1150 | 1150 | 1.0407
Critical Load Level | Transformer Max 2.5 MVA |  |  | 2015 | [5 empty] | 2014 | 1080 | 1085 | 1090 | 1100 | 1120 | 1125 | 1145 | 1150 | 1165 | 1170 | 1.0402
Load Reduction Needed | See Column I to the right |  |  | 2016 | [5 empty] | 2015 | 1095 | 1100 | 1105 | 1115 | 1135 | 1140 | 1160 | 1165 | 1170 | 1180 | 1.0308
Load Reduction Needed from EE |  | recognizing that NTA option might include a number of different NTAs which EE is one. Provide forecast information. Does forecast assume statewide EE programs already? |  | 2017 | [5 empty] | 2016 | 1105 | 1110 | 1115 | 1125 | 1145 | 1150 | 1170 | 1175 | 1190 | 1195 | 1.0393
Relavent VSPC Load Zone Maximum Achievable Savings Potential |  | From EEU achievable potential study |  | 2018 |  |  |  |  | Explanation of "High Scenario" parameters: | 2017 | 1115 | 1120 | 1125 | 1135 | 1155 | 1160 | 1180 | 1185 | 1195 | 1205 | 1.0346
Annual Exposure Duration (hours) |  | Attach documents as appropriate |  | 2019 | [5 empty] | 2018 | 1125 | 1130 | 1140 | 1150 | 1170 | 1175 | 1195 | 1200 | 1215 | 1215 | 1.0385
Constrained Area Peak Time of Day |  | range acceptable |  | 2020 | [5 empty] | 2019 | 1135 | 1140 | 1150 | 1160 | 1180 | 1185 | 1205 | 1210 | 1225 | 1230 | 1.0381
Estimated Year Project Needed absent GT | From Columns E-I to right when Cell B 14 critical load level > column H | If 2 years or less, then may not be viable for GT. If over 10 years, then may not be viable for GT. |  | 2021 | [5 empty] | 2020 | 1145 | 1150 | 1155 | 1170 | 1190 | 1195 | 1215 | 1225 | 1235 | 1240 | 1.0378
Estimated Project Cost $ |  | Use current year $ |  | 2022 | [5 empty] | WINTER
Benefit Classification |  | Use VSPC classification of system level and affected utilities - see 7081 definitions |  | 2023 |  |  |  |  | Note 3 - Incremental GT EE Needed should be defined as the level of incremental EE needed to keep the forecasted load below the critical load level | 2011/2012 | 1030 | 1035 | 1035 | 1035 | 1045 | 1050 | 1055 | 1055 | 1060 | 1070 | 1.0144
Estimated Annual Deferral Value |  | to determine real levelized carrying charge use method as defined in Docket 7081 MOU paragraph 63 |  | 2024 | [5 empty] | 2012/2013 | 1040 | 1045 | 1045 | 1045 | 1055 | 1060 | 1065 | 1065 | 1070 | 1080 | 1.0142
|  |  |  | 2025 | [5 empty] | 2013/2014 | 1050 | 1055 | 1055 | 1055 | 1065 | 1070 | 1075 | 1075 | 1080 | 1095 | 1.0141
Deferral Value |  |  |  | 2026 | [5 empty] | 2014/2015 | 1055 | 1060 | 1060 | 1060 | 1070 | 1075 | 1080 | 1080 | 1085 | 1095 | 1.014
Number of Years EE is able to defer project |  |  |  | 2027 | [5 empty] | 2015/2016 | 1060 | 1065 | 1065 | 1065 | 1075 | 1080 | 1085 | 1085 | 1090 | 1110 | 1.014
Value of deferment |  |  |  | 2028 | [5 empty] | 2016/2017 | 1065 | 1070 | 1070 | 1070 | 1080 | 1085 | 1090 | 1090 | 1100 | 1110 | 1.0185
Value of any additional T&D benefits provided by EE |  | e.g. reducing risk of contingencies, etc. Describe - could be narrative |  | 2029 | [5 empty] | 2017/2018 | 1075 | 1080 | 1080 | 1080 | 1090 | 1095 | 1100 | 1100 | 1105 | 1120 | 1.0138
reducing risk of unanticipated load coming on-line |  |  |  | 2030 | [5 empty] | 2018/2019 | 1080 | 1085 | 1085 | 1085 | 1095 | 1100 | 1105 | 1105 | 1110 | 1120 | 1.0137
reducing existing exposure on bulk transmission system |  |  |  | 2031 | [5 empty] | 2019/2020 | 1085 | 1090 | 1090 | 1090 | 1100 | 1105 | 1110 | 1110 | 1115 | 1125 | 1.0136
reducing existing exposure on subtransmission system | [9 empty] | 2020/2021 | 1090 | 1095 | 1095 | 1095 | 1105 | 1110 | 1115 | 1115 | 1120 | 1130 | 1.0136
reducing existing exposure on distribution system
Back to Main Page

## Hinesburg 19 (hidden)
Updated 05/21/2019 |  |  | RECOMMENDATION: This project is excluded from NTA analysis per the Docket 6290 screening tool. Upgrade being deffered indefinetly
Blue Background = Info provided by DU
Orange Background = Info provided by EEU
Instructions
Information regarding the constraint
T&D Constraint Name | Hinesburg 19
Primary Justification | Asset Management (Age and Condition)
Description of Constraint | Substation upgrade is driven by advanced substation age and deteriorating asset condition and cannot be avoided or deferred with non-traditional alternatives. The substation is also built on an existin wetland and next to ledge and as a result cannot be rebuilt on site. As a result, GMP and VEC have begun discussions on the possibility of constructing a jointly-owned substation. VEC notes that, in recent years, GMP and VEC have successfully collaborated on three joint substation ventures including the Richmond, Jay, and Tafts Corner distribution substations. VEC also notes that such collaboration is required by the Department of Public Service (Department) Vermont Electric Plan.
Description of Upgrade | VEC has not yet determined a final configuration for the joint project. The substation will be rebuilt with GMP on a new site. GMP will split the cost, design, permitting, and construction of the project with VEC. This project consists of two GMP distribution circuits and three VEC distribution circuits with associated circuit breakers, regulators, steel and foundations, dual 10/14 MVA distribution power transformer with oil containment, a high side circuit breaker, and associated fence, ground grid, communication and security work. |  |  | Forecasted load and EE Incremental to Statewide
VSPC Load Zone | I | Could be one or more |  | Critical Load Level |  |  |  | Transformer Max 7.5 MVA | From Cell B14 | VT
Season of Issue | Both | Winter, Summer, or Both |  | Year | 50/50 forecast (MW) [N2] | 90/10 forecast (MW) [N1] | "High Scenario" (MW) | Incremental GT EE needed [N3] | Note 1- use CELT forecast 50/50 to 90/10 ratio provided to the right for relevant ratio. Carry 2020 ratio out for 10 years | SUMMER | 90% | 80% | 70% | 60% | 50% | 40% | 30% | 20% | 10% | 5% | 1950-10-01
Most Recent Peak Load | 4.706 MVA (2/8/2015 6:00:00 PM) |  |  | 2012 | [5 empty] | 2011 | 1030 | 1035 | 1040 | 1050 | 1070 | 1075 | 1090 | 1095 | 1110 | 1110 | 1.0374
5-year historical maximum peak Load | 4.706 MVA (2/8/2015 6:00:00 PM) |  |  | 2013 |  |  |  |  | Note 2 - these loads should already be adjusted for EE included in the trend forecast (removed per EVT reports for every year of the weighted average) then statewide expected savings added (per VEIC calculation, PSB ordered budgets) | 2012 | 1050 | 1055 | 1060 | 1070 | 1090 | 1095 | 1115 | 1120 | 1125 | 1135 | 1.0321
Known additional load | None | e.g. from "Ability to Serve" letters |  | 2014 | [5 empty] | 2013 | 1065 | 1070 | 1075 | 1085 | 1105 | 1110 | 1130 | 1135 | 1150 | 1150 | 1.0407
Critical Load Level | Transformer Max 7.5 MVA |  |  | 2015 | [5 empty] | 2014 | 1080 | 1085 | 1090 | 1100 | 1120 | 1125 | 1145 | 1150 | 1165 | 1170 | 1.0402
Load Reduction Needed | See Column I to the right |  |  | 2016 | [5 empty] | 2015 | 1095 | 1100 | 1105 | 1115 | 1135 | 1140 | 1160 | 1165 | 1170 | 1180 | 1.0308
Load Reduction Needed from EE |  | recognizing that NTA option might include a number of different NTAs which EE is one. Provide forecast information. Does forecast assume statewide EE programs already? |  | 2017 | [5 empty] | 2016 | 1105 | 1110 | 1115 | 1125 | 1145 | 1150 | 1170 | 1175 | 1190 | 1195 | 1.0393
Relavent VSPC Load Zone Maximum Achievable Savings Potential |  | From EEU achievable potential study |  | 2018 |  |  |  |  | Explanation of "High Scenario" parameters: | 2017 | 1115 | 1120 | 1125 | 1135 | 1155 | 1160 | 1180 | 1185 | 1195 | 1205 | 1.0346
Annual Exposure Duration (hours) |  | Attach documents as appropriate |  | 2019 | [5 empty] | 2018 | 1125 | 1130 | 1140 | 1150 | 1170 | 1175 | 1195 | 1200 | 1215 | 1215 | 1.0385
Constrained Area Peak Time of Day |  | range acceptable |  | 2020 | [5 empty] | 2019 | 1135 | 1140 | 1150 | 1160 | 1180 | 1185 | 1205 | 1210 | 1225 | 1230 | 1.0381
Estimated Year Project Needed absent GT | From Columns E-I to right when Cell B 14 critical load level > column H | If 2 years or less, then may not be viable for GT. If over 10 years, then may not be viable for GT. |  | 2021 | [5 empty] | 2020 | 1145 | 1150 | 1155 | 1170 | 1190 | 1195 | 1215 | 1225 | 1235 | 1240 | 1.0378
Estimated Project Cost $ |  | Use current year $ |  | 2022 | [5 empty] | WINTER
Benefit Classification |  | Use VSPC classification of system level and affected utilities - see 7081 definitions |  | 2023 |  |  |  |  | Note 3 - Incremental GT EE Needed should be defined as the level of incremental EE needed to keep the forecasted load below the critical load level | 2011/2012 | 1030 | 1035 | 1035 | 1035 | 1045 | 1050 | 1055 | 1055 | 1060 | 1070 | 1.0144
Estimated Annual Deferral Value |  | to determine real levelized carrying charge use method as defined in Docket 7081 MOU paragraph 63 |  | 2024 | [5 empty] | 2012/2013 | 1040 | 1045 | 1045 | 1045 | 1055 | 1060 | 1065 | 1065 | 1070 | 1080 | 1.0142
|  |  |  | 2025 | [5 empty] | 2013/2014 | 1050 | 1055 | 1055 | 1055 | 1065 | 1070 | 1075 | 1075 | 1080 | 1095 | 1.0141
Deferral Value |  |  |  | 2026 | [5 empty] | 2014/2015 | 1055 | 1060 | 1060 | 1060 | 1070 | 1075 | 1080 | 1080 | 1085 | 1095 | 1.014
Number of Years EE is able to defer project |  |  |  | 2027 | [5 empty] | 2015/2016 | 1060 | 1065 | 1065 | 1065 | 1075 | 1080 | 1085 | 1085 | 1090 | 1110 | 1.014
Value of deferment |  |  |  | 2028 | [5 empty] | 2016/2017 | 1065 | 1070 | 1070 | 1070 | 1080 | 1085 | 1090 | 1090 | 1100 | 1110 | 1.0185
Value of any additional T&D benefits provided by EE |  | e.g. reducing risk of contingencies, etc. Describe - could be narrative |  | 2029 | [5 empty] | 2017/2018 | 1075 | 1080 | 1080 | 1080 | 1090 | 1095 | 1100 | 1100 | 1105 | 1120 | 1.0138
reducing risk of unanticipated load coming on-line |  |  |  | 2030 | [5 empty] | 2018/2019 | 1080 | 1085 | 1085 | 1085 | 1095 | 1100 | 1105 | 1105 | 1110 | 1120 | 1.0137
reducing existing exposure on bulk transmission system |  |  |  | 2031 | [5 empty] | 2019/2020 | 1085 | 1090 | 1090 | 1090 | 1100 | 1105 | 1110 | 1110 | 1115 | 1125 | 1.0136
reducing existing exposure on subtransmission system | [9 empty] | 2020/2021 | 1090 | 1095 | 1095 | 1095 | 1105 | 1110 | 1115 | 1115 | 1120 | 1130 | 1.0136
reducing existing exposure on distribution system
Back to Main Page

## PHASE 2 Template
Paste template from Area 1 when complete
Information regarding the affected customers
Total Premises affected
Total MW of premises | premises = "constrained area"
Total MWh of premises
Total # of industrial premises | Provide definition of "Industrial" customers
Total MW from industrial premises | If only 1 industrial customer, include with commercial
Total MWh from industrial premises
Total # of commercial premises
Total MW from commercial premises
Total MWh from commercial premises
Total # of residential premises
Total Estimated MW from residential premises | Use/provide assumptions regarding load factor
Total MWh from residential premises
Information regarding Energy Efficiency Potential | To be completed following submittal of above infomration
Achievable Cost-Effective Energy Efficeincy Potential in Area | Provide summary of how potential is estimated and assumed to be acquired - this should be rough estimate
Estimate of statewide programs efficiency acquisition MW
Estimate of statewide programs efficiency acquisition MWh
Estimate of incremental available potential | breakdown res/commercial?
Cost to deliver EE to targeted area $/kW
Cost to deliver statewide EE to that targeted area $/kW | Programs would have been delivered anyway in area
Total cost above status quo to deliver GT program
Estimated probability of success | Above a certain percentage, the go forward with GT